400 Watts

MONOCRYSTALLINE SOLAR MODULE

Products features:

- High efficiency cell

- Multi-bus grid technology

- Strong aluminum alloy frame

- Standard tolerance (Guaranteed standard tolerance from -3~+3% ensures power output reliability)

- Excellent weak light performance

Excellent performance under low light environments (mornings, evenings, and cloudy days)

- Withstand high wind and snow loads

Entire module certified to withstand high wind loads (2400 Pascal) and snow loads (5400 Pascal)

Electrical Characteristics

| Model No. | SFM-400W |
| --- | --- |
| Maximum Power at STC (Pmax) | 400W |
| Optimum Operating Voltage (Vmp) | 34.3V |
| Open - Circuit Voltage (Voc) | 41.6V |
| Optimum Operating Current (Imp) | 11.66A |
| Short - Circuit Current (Isc) | 12.83A |
| Cell Efficiency | 20.5% |
| Operating Module Temperature | -40 °C to +85 °C |
| Maximum System Voltage | 1000 V DC (IEC) / 600 V DC (UL) |
| Diodes | 3 by pass |
| Power Tolerance | -3/+3 % |

STC: irradiance 1000 W/m2, module temperature 25 °C, AM=1.5; Power measurement tolerance: ± 3%

Mechanical Characteristics

| Solar Cell | Monocrystalline 166*83mm |
| --- | --- |
| No. of Cells | 120(6× 20) |
| Dimensions | 1755*1038*35 mm |
| Weight | 20Kgs |
| Front Glass | 3.2 mm (0.13 inches) tempered glass |
| Frame | Anodized aluminum alloy |
| Junction Box | IP65 rated |
| Output Cables | TUV |
|  | 4.0 mm2 (0.16inches2), symmetrical lengths (-) 900 mm (35.4 inches) and (+) 900 mm (35.4 inches) |
| Connectors | RADOX® SOLAR integrated twist locking connectors |

Temperature Characteristics

| Nominal Operating Cell Temperature (NOCT) | 45±2 ℃ |
| --- | --- |
| Temperature Coefficient of Pmax | -0.35%/℃ |
| Temperature Coefficient of Voc | -0.276%/℃ |
| Temperature Coefficient of Isc | 0.045%/℃ |

Quality and Safety:

Product warranty:

Singfo Solar modules will last for at least 25 years.

Free from defects in material and workmanship for 5 years.

All the panels passed IEC, TUV standards.

Power warranty:

Maintain more than 90% of minimum rated power for 10 years.

Maintain more than 80% of minimum rated power for 25 years.